[image: image1.wmf]
Ventilation Checklist


Name: 

School: 


Unit Ventilator/AHU No: 

Room or Area: 

Date Completed: 

Signature: 



Instructions

1.  Read the IAQ 
Backgrounder and 
the Background 
Information for 
this checklist.

2.  Keep the 
Background 
Information and 
make a copy of 
the checklist for each ventilation unit in your school, as well as a copy for future reference.

3.  Complete the 
Checklist.

•
Check the “yes,” 
“no,” or 
“not applicable” 
box beside each 
item. (A “no” 
response 
requires further 
attention.)

•
Make comments 
in the “Notes” 
section as 
necessary.

4.  Return the checklist 
portion of this 
document to the 
IAQ Coordinator.

	

1.
OUTDOOR AIR INTAKES

1a.
Marked locations of all outdoor air intakes on a small floor plan (for              Yes
No
N/A
example, a fire escape floor plan)




1b.
Ensured that the ventilation system was on and operating in “occupied” 
mode



Activity 1: Obstructions
1c.
Ensured that outdoor air intakes are clear of obstructions, debris, clogs, 
or covers



1d.
Installed corrective devices as necessary (e.g., if snowdrifts or leaves 
frequently block an intake)



Activity 2: Pollutant Sources
1e.
Checked ground-level intakes for pollutant sources (dumpsters, loading 
docks, and bus-idling areas)



1f.
Checked rooftop intakes for pollutant sources (plumbing vents; kitchen, 
toilet, or laboratory exhaust fans; puddles; and mist from 
air-conditioning cooling towers)



1g.
Resolved any problems with pollutant sources located near outdoor air 
intakes (e.g., relocated dumpster or extended exhaust pipe)



Activity 3: Airflow
1h.
Obtained chemical smoke (or a small piece of tissue paper or light plastic)



1i.
Confirmed that outdoor air is entering the intake appropriately



2.
SYSTEM CLEANLINESS
Activity 4: Air Filters
2a.
Replaced filters per maintenance schedule



2b.
Shut off ventilation system fans while replacing filters (prevents dirt from 
blowing downstream)



2c.
Vacuumed filter areas before installing new filters



2d.
Confirmed proper fit of filters to prevent air from bypassing (flowing
around) the air filter



2e.
Confirmed proper installation of filters (correct direction for airflow)




	


2.
SYSTEM CLEANLINESS (continued)
Activity 5: Drain Pans
2f.
Ensured that drain pans slant toward the drain (to prevent water from          Yes
No
N/A
accumulating) 



2g.
Cleaned drain pans



2h.
Checked drain pans for mold and mildew



Activity 6: Coils
2i.
Ensured that heating and cooling coils are clean



Activity 7: Air-Handling Units, Unit Ventilators
2j.
Ensured that the interior of air-handling unit(s) or unit ventilator
(air-mixing chamber and fan blades) is clean



2k.
Ensured that ducts are clean



Activity 8: Mechanical Rooms
2l. 
Checked mechanical room for unsanitary conditions, leaks, and spills



2m.
Ensured that mechanical rooms and air-mixing chambers are free of trash, 
chemical products, and supplies



3.
CONTROLS FOR OUTDOOR AIR SUPPLY

3a.
Ensured that air dampers are at least partially open (minimum position)



3b.
Ensured that minimum position provides adequate outdoor air 
for occupants



Activity 9: Controls Information
3c.
Obtained and reviewed all design inside/outside temperature and humidity 
requirements, controls specifications, as-built mechanical drawings, 
and controls operations manuals (often uniquely designed)



Activity 10: Clocks, Timers, Switches
3d.
Turned summer-winter switches to the correct position



3e.
Set time clocks appropriately



3f.
Ensured that settings fit the actual schedule of building use (including 
night/weekend use)



Activity 11: Control Components
3g.
Ensured appropriate system pressure by testing line pressure at both the 
occupied (day) setting and the unoccupied (night) setting



3h.
Checked that the line dryer prevents moisture buildup



3i. 
Replaced control system filters at the compressor inlet based on the 
compressor manufacturer’s recommendation (for example, when you 
blow down the tank)



3j.
Set the line pressure at each thermostat and damper actuator at the proper 
level (no leakage or obstructions)



Activity 12: Outdoor Air Dampers
3k.
Ensured that the outdoor air damper is visible for inspection



3l. 
Ensured that the recirculating relief and/or exhaust dampers are visible 
for inspection



3m.
Ensured that air temperature in the indoor area(s) served by each 
outdoor air damper is within the normal operating range



NOTE: It is necessary to ensure that the damper is operating properly and within the normal range to continue.



3.
CONTROLS FOR OUTDOOR AIR SUPPLY (continued)

3n.
Checked that the outdoor air damper fully closes within a few minutes          Yes
No
N/A
of shutting off appropriate air handler



3o.
Checked that the outdoor air damper opens (at least partially with no
delay) when the air handler is turned on



3p.
If in heating mode, checked that the outdoor air damper goes to its 
minimum position (without completely closing) when the room 
thermostat is set to 85°F



3q.
If in cooling mode, checked that the outdoor air damper goes to its 
minimum position (without completely closing) when the room thermostat 
is set to 60°F and mixed air thermostat is set to 45°F



3r.
If the outdoor air damper does not move, confirmed the following items:


•
The damper actuator links to the damper shaft, and any linkage set 
screws or bolts are tight




•
Moving parts are free of impediments (e.g., rust, corrosion)




•
Electrical wire or pneumatic tubing connects to the damper actuator




•
The outside air thermostat(s) is functioning properly (e.g., in the right 
location, calibrated correctly)



Proceed to Activities 13–16 if the damper seems to be operating properly.

Activity 13: Freeze Stats
3s.
Disconnected power to controls (for automatic reset only) to test continuity 
across terminals



OR

3t.
Confirmed (if applicable) that depressing the manual reset button (usually 
red) trips the freeze stat (clicking sound indicates freeze stat was 
tripped)



3u.
Assessed the feasibility of replacing all manual reset freeze-stats with 
automatic reset freeze-stats



NOTE: HVAC systems with water coils need protection from the cold. The freeze-stat may close the outdoor air damper and disconnect the supply air when tripped. The typical trip range is 35°F to 42°F.

Activity 14: Mixed Air Thermostats
3v.
Ensured that the mixed air stat for heating mode is set no higher 
than 65°F



3w.
Ensured that the mixed air stat for cooling mode is set no lower 
than the room thermostat setting



Activity 15: Economizers
3x.
Confirmed proper economizer settings based on design specifications or 
local practices



NOTE: The dry-bulb is typically set at 65°F or lower.

3y.
Checked that sensor on the economizer is shielded from direct sunlight



3z.
Ensured that dampers operate properly (for outside air, return air, 
exhaust/relief air, and recirculated air), per the design specifications



NOTE: Economizers use varying amounts of cool outdoor air to assist with the cooling 
load of the room or rooms. There are two types of economizers, dry-bulb and enthalpy. 
Dry-bulb economizers vary the amount of outdoor air based on outdoor temperature, 
and enthalpy economizers vary the amount of outdoor air based on outdoor temperature 
and humidity level.

3.
CONTROLS FOR OUTDOOR AIR SUPPLY (continued)
Activity 16: Fans
3aa.
Ensured that all fans (supply fans and associated return or relief fans) 
that move outside air indoors continuously operate during occupied             Yes
No
N/A
hours (even when room thermostat is satisfied) 



NOTE: If fan shuts off when the thermostat is satisfied, adjust control cycle as necessary to ensure sufficient outdoor air supply.

4.
AIR DISTRIBUTION
Activity 17: Air Distribution
4a.
Ensured that supply and return air pathways in the existing ventilation system 
perform as required



4b.
Ensured that passive gravity relief ventilation systems and transfer grilles 
between rooms and corridors are functioning 



NOTE: If ventilation system is closed or blocked to meet current fire codes, consult with a professional engineer for remedies.

4c.
Made sure every occupied space has supply of outdoor air (mechanical 
system or operable windows)



4d.
Ensured that supply and return vents are open and unblocked



NOTE: If outlets have been blocked intentionally to correct drafts or discomfort, investigate and correct the cause of the discomfort and reopen the vents.
4e.
Modified the HVAC system to supply outside air to areas without an outdoor 
air supply



4f.
Modified existing HVAC systems to incorporate any room or zone layout 
and population changes



4g.
Moved all barriers (for example, room dividers, large free-standing 
blackboards or displays, bookshelves) that could block movement of 
air in the room, especially those blocking air vents



4h.
Ensured that unit ventilators are quiet enough to accommodate classroom 
activities



4i.
Ensured that classrooms are free of uncomfortable drafts produced by air 
from supply terminals



Activity 18: Pressurization in Buildings
NOTE: To prevent infiltration of outdoor pollutants, the ventilation system is designed to maintain positive pressurization in the building. Therefore, ensure that the system, including any exhaust fans, is operating on the “occupied” cycle when doing this activity.
4j.
Ensured that air flows out of the building (using chemical smoke) through 
windows, doors, or other cracks and holes in exterior wall (for example, 
floor joints, pipe openings)



5.
EXHAUST SYSTEMS

Activity 19: Exhaust Fan Operation
5a.
Checked (using chemical smoke) that air flows into exhaust fan grille(s)



If fans are running but air is not flowing toward the exhaust intake, check for the following:


•
Inoperable dampers


•
Obstructed, leaky, or disconnected ductwork


•
Undersized or improperly installed fan


•
Broken fan belt


NOTES

5.
EXHAUST SYSTEMS (continued)

Activity 20: Exhaust Airflow
NOTE: Prevent migration of indoor contaminants from areas such as bathrooms, kitchens, and labs by keeping them under negative pressure (as compared to surrounding spaces).

5b. 
Checked (using chemical smoke) that air is drawn into the room                 Yes
No
N/A
from adjacent spaces



Stand outside the room with the door slightly open while checking airflow high and low in the door opening (see “How to Measure Airflow”).
5c. Ensured that air is flowing toward the exhaust intake



Activity 21: Exhaust Ductwork
5d. 
Checked that the exhaust ductwork downstream of the exhaust fan 
(which is under positive pressure) is sealed and in good condition



6.
QUANTITY OF OUTDOOR AIR
Activity 22: Outdoor Air Measurements and Calculations
NOTE: Refer to “How to Measure Airflow” for techniques.
6a. 
Measured the quantity of outdoor air supplied (22a) to each ventilation 
unit



6b. 
Calculated the number of occupants served (22b) by the ventilation unit 
under consideration



6c. 
Divided outdoor air supply (22a) by the number of occupants (22b) to 
determine the existing quantity of outdoor air supply per person (22c)



Activity 23: Acceptable Levels of Outdoor Air Quantities
6d. 
Compared the existing outdoor air per person (22c) to the recommended 
levels in Table 1



6e. 
Corrected problems with ventilation units that supplied inadequate 
quantities of outdoor air to ensure that outdoor air quantities (22c) 
meet the recommended levels in Table 1



1 of 5





2 of 5





3 of 5





4 of 5





5 of 5








